- Install “FlashH08” Flash Program

Run the “Flash3062_B” program to install “FlashH08” flash software, you will get the instructions step by step. (Any number can be register number)

- Use “FlashH08 ” to flash CPU

Step1: Terminate those software which already occupied COM1 of PC, Ex:UPSMon, UPS monitor application

Step2: Check “CPU Version” of the LCD display in the front panel

Step3: Connect RS232 cable to UPS from “COM1” of PC (It must use “COM1” as default communication port)

Step4: Turn UPS off and still keep AC Line On

Step5: Run “FlashH08 application” which you have already installed in process (A) and it should look like the following

Step6: Press“Load” item in the Menu to Load the file (*.mot) you want to reflash to CPU

Step7: Press “ALL” button in Toolbar and it will start the “Flash Process”. During this period, “Back light front panel” are turned off

Note:

1. If communication fail during “Flash  Process”, “Flash3062_B” will show “Time out”,  user should wait more than 30 seconds, and then press “W” button in Toolbar to start “Flash Process” again.

2. Don’t run any other “Application Software” on PC during “Flash Process”, because “FlashH08 application” need a lot of PC resource

3. Unplug the snmpcard from the slot is necessary